{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["08上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2025.08.04","新村西路140号原市水资办","20250804-0645",16,"未检出","<5","0.31","无","无",0.04,"/","2025.08.06"," 王晓芳"]
[2,"2025.08.04","淄博市政务中心","20250804-0646",7,"未检出","<5","0.34","无","无",0.04,"/","2025.08.06"," 王晓芳"]
[3,"2025.08.04","张店区疾控中心","20250804-0647",21,"未检出","<5","0.32","无","无",0.05,"/","2025.08.06"," 王晓芳"]
[4,"2025.08.04","西苑社区","20250804-0648",10,"未检出","<5","0.29","无","无",0.03,"/","2025.08.06"," 王晓芳"]
[5,"2025.08.04","五公里党群站","20250804-0649",25,"未检出","<5","0.17","无","无",0.03,0.92,"2025.08.06"," 王晓芳"]
[6,"2025.08.04","   市自来水公司南定营销服务中心","20250804-0650",11,"未检出","<5","0.32","无","无",0.04,0.97,"2025.08.06"," 王晓芳"]
[7,"2025.08.04","市自来水公司铝城营业所","20250804-0651",44,"未检出","<5","0.35","无","无",0.03,"/","2025.08.06"," 王晓芳"]
[8,"2025.08.04","经开区后南定村卫生室","20250804-0652",23,"未检出","<5","0.23","无","无",0.03,"/","2025.08.06"," 王晓芳"]
[9,"2025.08.04","张南路101号中石油加油站","20250804-0653",5,"未检出","<5","0.21","无","无",0.05,"/","2025.08.06"," 王晓芳"]
[10,"2025.08.04","山泉路启星比亚迪4S店","20250804-0654",2,"未检出","<5","0.25","无","无",0.04,"/","2025.08.06"," 王晓芳"]
[11,"2025.08.11","天勤苑社区","20250811-0655",23,"未检出","<5","0.27","无","无",0.04,1.05,"2025.08.13"," 王晓芳"]
[12,"2025.08.11","高新区金晶大道汇驰奔驰4S店","20250811-0656","未检出","未检出","<5","0.29","无","无",0.03,"/","2025.08.13"," 王晓芳"]
[13,"2025.08.11","金都花园社区","20250811-0657",1,"未检出","<5","0.13","无","无",0.04,0.95,"2025.08.13"," 王晓芳"]
[14,"2025.08.11","星悦城社区","20250811-0658",4,"未检出","<5","0.22","无","无",0.03,0.91,"2025.08.13"," 王晓芳"]
[15,"2025.08.11","外商居住区","20250811-0659",2,"未检出","<5","0.26","无","无",0.04,"/","2025.08.13"," 王晓芳"]
[16,"2025.08.11","市自来水开发区营业所","20250811-0660",2,"未检出","<5","0.24","无","无",0.05,"/","2025.08.13"," 王晓芳"]
[17,"2025.08.11","淄博市十一中","20250811-0661",3,"未检出","<5","0.27","无","无",0.03,"/","2025.08.13"," 王晓芳"]
[18,"2025.08.11","丽莎会议中心","20250811-0662",37,"未检出","<5","0.19","无","无",0.02,"/","2025.08.13"," 王晓芳"]
[19,"2025.08.11","华侨城警务室","20250811-0663",6,"未检出","<5","0.38","无","无",0.04,"/","2025.08.13"," 王晓芳"]
[20,"2025.08.12","淄博市委","20250812-0664",5,"未检出","<5","0.30","无","无",0.03,"/","2025.08.14"," 王晓芳"]
[21,"2025.08.12","张店区军休所","20250812-0665",31,"未检出","<5","0.32","无","无",0.04,"/","2025.08.14"," 王晓芳"]
[22,"2025.08.12","五里桥生活区","20250812-0666",5,"未检出","<5","0.23","无","无",0.05,"/","2025.08.14"," 王晓芳"]
[23,"2025.08.12","祥瑞花园社区","20250812-0667",29,"未检出","<5","0.22","无","无",0.03,"/","2025.08.14"," 王晓芳"]
[24,"2025.08.12","张店八中","20250812-0668",19,"未检出","<5","0.21","无","无",0.04,"/","2025.08.14"," 王晓芳"]
[25,"2025.08.12","淄博市图书馆","20250812-0669",2,"未检出","<5",0.27,"无","无",0.05,"/","2025.08.14"," 王晓芳"]
[26,"2025.08.12","积家村党群服务中心","20250812-0670",7,"未检出","<5","0.29","无","无",0.04,1.17,"2025.08.14"," 王晓芳"]
[27,"2025.08.12","明德苑社区","20250812-0671",12,"未检出","<5","0.17","无","无",0.03,"/","2025.08.14"," 王晓芳"]
[28,"2025.08.13","恒嘉园社区","20250813-0672",1,"未检出","<5","0.32","无","无",0.04,"/","2025.08.15"," 王晓芳"]
[29,"2025.08.13","人民东路小学","20250813-0673",11,"未检出","<5","0.34","无","无",0.04,"/","2025.08.15"," 王晓芳"]
[30,"2025.08.13","张店区保安公司","20250813-0674",2,"未检出","<5","0.24","无","无",0.03,"/","2025.08.15"," 王晓芳"]
[31,"2025.08.13","润德实业公司","20250813-0675","未检出","未检出","<5","0.25","无","无",0.05,"/","2025.08.15"," 王晓芳"]
[32,"2025.08.13","行政执法局湖田中队","20250813-0676",7,"未检出","<5","0.32","无","无",0.04,"/","2025.08.15"," 王晓芳"]
[33,"2025.08.13","淄博市公交东站","20250813-0677",2,"未检出","<5","0.24","无","无",0.05,"/","2025.08.15"," 王晓芳"]
[34,"2025.08.13","洪三社区","20250813-0678",5,"未检出","<5","0.31","无","无",0.04,1.05,"2025.08.15"," 王晓芳"]
[35,"2025.08.14","淄博市工商局","20250814-0679",46,"未检出","<5","0.31","无","无",0.03,"/","2025.08.16"," 王晓芳"]
[36,"2025.08.14","市自来水公司新区营业所","20250814-0680",19,"未检出","<5","0.23","无","无",0.04,"/","2025.08.16"," 王晓芳"]
[37,"2025.08.14","颐臻园社区","20250814-0681",9,"未检出","<5","0.29","无","无",0.04,"/","2025.08.16"," 王晓芳"]
[38,"2025.08.14","世纪花园社区","20250814-0682",12,"未检出","<5","0.32","无","无",0.03,"/","2025.08.16"," 王晓芳"]
[39,"2025.08.14","瑞丰苑社区","20250814-0683",4,"未检出","<5","0.33","无","无",0.03,1.13,"2025.08.16"," 王晓芳"]
[40,"2025.08.14","科技苑物业","20250814-0684",33,"未检出","<5","0.31","无","无",0.04,"/","2025.08.16"," 王晓芳"]
[41,"2025.08.15","淄博市体育馆","20250815-0685",19,"未检出","<5","0.30","无","无",0.05,"/","2025.08.17"," 王晓芳"]
[42,"2025.08.15","福源汇社区","20250815-0686",5,"未检出","<5","0.33","无","无",0.04,"/","2025.08.17"," 王晓芳"]
[43,"2025.08.15","孝妇河湿地公园喷泉广场","20250815-0687",1,"未检出","<5","0.27","无","无",0.03,1.19,"2025.08.17"," 王晓芳"]
[44,"2025.08.15","石家社区","20250815-0688",7,"未检出","<5","0.30","无","无",0.04,1.11,"2025.08.17"," 王晓芳"]
[45,"2025.08.15","盛世康城社区","20250815-0689",9,"未检出","<5","0.32","无","无",0.03,"/","2025.08.17"," 王晓芳"]
[46,"2025.08.15","福瑞家园社区","20250815-0690",3,"未检出","<5","0.23","无","无",0.04,1.05,"2025.08.17"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}